## Sheet1
TOOL FOR DESIGN OF STP BASED ON ANAEROBIC AND FACULTATIVE PONDS
Capacity Average Flow |  | 25 | MLD
Guidance: Yellow cells are the input information to be suitably filled. Green cells are to be reviewed and modified/updated if need be. Red letters to be suitably corrected.
Ground level at STP Site at Inlet chamber |  |  |  | 209.5 | Mtr
Drain level at outlet at chainage 11325 |  |  |  | 206.2 | Mtr
IL of Out fall Sewer(1000 mm) with slope 1 in 1100 at STP |  |  |  | 215.68 | Mtr
Average Flow |  |  |  | 25 | MLD
Average Flow |  |  |  | 0.28935 | M3/sec
Peak Flow : | Peak Factor |  | 2.25 | 56.25 | MLD
Peak Flow : |  |  |  | 0.65104 | M3/sec
Minimum Flow |  | Factor | 2 | 12.5 | MLD
Minimum Flow |  |  |  | 0.14468 | M3/sec
DESIGN OF INLET CHAMBER
Peak Flow |  |  |  | 56.25 | MLD
Peak Flow |  |  |  | 0.65104 | M3/sec
Detention time |  |  |  | 15 | Sec
Volume required |  |  |  | 9.7656 | cum
Liquid depth taken |  |  |  | 0.8 | Mtr
Area |  |  |  | 12.207 | M2
Width taken |  |  |  | 3.4939 | Mtr
Length |  |  |  | 3.4939 | Mtr
Provide free board to ensure that raw sewage will not overflow even when the 1000 mm out fall sewer run full |  |  |  | 0.8 | Mtr
DESIGN OF COARSE SCREEN
Peak Flow |  |  |  | 0.65104 | M3/sec
Coarse Screen Opening |  |  |  | 50 | mm
Depth of water in screen |  |  |  | 0.9 | Mtr.
velocity through screen |  |  |  | 0.7 | M/sec
Area of screen |  |  |  | 0.93006 | M2
Angle of inclination with the horizontal |  |  |  | 45 | degree
Sin (Angle of Inclination) |  |  |  | 0.70739
Free Board |  |  |  | 0.6 | m
Length of screen |  |  |  | 2.1205
Width of opening |  |  |  | 1.0334 | mtr
No of opening |  |  |  | 20.668 | nos
Number of bars |  |  |  | 19.668 | nos
Let width of each bar be |  |  |  | 10 | mmx75 mm
Total width of channel |  |  |  | 1230.0794 | mm
Let width of each side be |  |  |  | 50 | mm
Total width of channel: Provide |  |  |  | 1331 | mm
Openings |  |  |  | 22.35
No of bars |  |  |  | 21.35
Size of Coarse Screen-Width |  |  |  | 1.331 | m
Size of Coarse Screen-Length |  |  |  | 4 | m
Velocity in Channal u/s of Screen |  |  |  | 0.54349
Velocity through Screen |  |  |  | 0.64732
Head Loss No Clogging |  |  |  | 0.006302 | m
Velocity when 50% clogging |  |  |  | 1.2946 | m/sec
Head Loss when 50% clogging |  |  |  | 0.070373 | m
DESIGN OF FINE SCREEN
Peak Flow |  |  |  | 0.65104 | M3/sec
Nos of screen(Each for handling peak flow) |  |  |  | 2 | Nos
Velocity(taking) through screen, Assume |  |  |  | 0.8 | M/sec
Area |  |  |  | 0.8138 | M2
Depth of flow taken |  |  |  | 0.7 | Mtr.
Hence width of opening |  |  |  | 1.1626 | Mtr.
No of Openings |  |  |  | 77.505
No of Bars |  |  |  | 76.505
Width of Channal |  |  |  | 1927.624
Angle of inclination with the horizontal |  |  |  | 75 | degree
Clear opening between adjacent bars of screen |  |  |  | 15 | mm
Bars thickness of screen |  |  |  | 10 | mm x50mm
Taking width of screen |  |  |  | 2000 | mm
Nos of opening will be |  |  |  | 80.4 | Nos
Nos of bars(10 mm thickness) |  |  |  | 79.4 | Nos
Free Board |  |  |  | 0.6 | m
Sin (Angle of Inclination with horizontal) |  |  |  | 0.96596
Inclined length of Screen |  |  |  | 1.3458 | m
Length of chamber before screen |  |  |  | 1.5 | m
Total Length of chamber |  |  |  | 2.8458
Total width of channel |  |  |  | 2 | Mtr.
Velocity in Channal u/s of Screen |  |  |  | 0.46503 | m/sec
Velocity through Screen |  |  |  | 0.77119 | m/sec
Head Loss through screen |  |  |  | 0.019291 | m
Velocity through screen when 50% clogged |  |  |  | 1.5424
Head Loss when 50% clogging |  |  |  | 0.11023
Size-2.85 (L)x2(W)x1.7(D)
DESIGN OF GRIT CHAMBER
GRIT REMOVAL SYSTEM
Two grit removal tank (1 w +1 S) each capable of handling peak flow, will be provided. They are designed to remove grit particle of size of 0.15 mm size and above with a specific gravity of 2.3
Q/A=VS x n/(1-η)-n-1
Where-η-Desired efficiency of removal of grit particle
VS -settling velocity of minimum size of grit particle to be removed
Q/A--Design surface overflow rate applicable for grit chamber to be designed
n-an index which a measure of the basin performance
Here η value taken |  |  |  | 75 | %
Say |  |  |  | 0.75
Here VS value taken |  |  |  | 1225 | m3/m2/day
Here n value taken-1/8(for very good performance) |  |  |  | 0.13
Hence surface over flow rate(Q/A)=(Vs*n)/(((1-η)^-n)-1) |  |  |  | 806.4161 | m3/m2/day
Say |  |  |  | 810 | m3/m2/day
This Q/A value has to be reduced to allow for deposition of sand during sand strom by |  |  |  | 10% | %
Then design overflow rate |  |  |  | 729 | m3/m2/day
Peak flow(m3/day) |  |  |  | 56250 | (m3/day)
Hence area required for peak flow |  |  |  | 77.1605 | m2
Each side of square grit chamber |  |  |  | 8.7841 | mtr.
Hence provide tank length |  |  |  | 9 | mtr.
Hence provide tank Width |  |  |  | 9 | mtr.
Detention time taken is |  |  |  | 1 | minute
Depth of tank will be |  |  |  | 0.48225 | mtr.
However in order to provide adequate depth for the grit scraping mechanism, increase to |  |  |  | 0.9 | mtr.
This gives detention time is |  |  |  | 1.8662 | minute
the detention time of 1.87(slightly higher) minute is immaterial for mechanically cleaned grit removal tank
Hence size of grit removal chamber is |  |  |  | 9 x9x0.9
Flow height above, H weir,Q=(2/3)*Cd*L*H^1.5*((2g)^.5),Cd=.6,L=9 |  |  |  | 0.11805 | m
DESIGN OF CHANNEL FROM GRIT CHAMBER TO DISTRIBUTION CHAMBER
Peak flow |  |  |  | 0.65104 | M3/sec
velocity taken |  |  |  | 0.8 | M/sec
Area required |  |  |  | 0.8138 | m2
Depth taken |  |  |  | 0.7 | mtr.
Then width of channel will be |  |  |  | 1.1626 | mtr.
DESIGN OF ANAEROBIC POND
No of Anaerobic ponds to provide flexibility in O&M of these ponds |  |  |  | 3 | Nos
Each handling flow of(25000m3 per day/3) |  |  |  | 8333.3333 | (m3/day)
say |  |  |  | 8333.3333 | (m3/day)
Volume of anaerobic pond V=Li xQ/λ
Li-Raw sewage BOD(1000 XB/q) |  |  |  | 300 | mg/l
Q- average flow |  |  |  | 8333.3333 | (m3/day)
λ- volumetric BOD loading(Range between 100-400 gm/m3/day)
λ=20T-100(as per MEAFNRCD)
T=mean temperature in coldest month in 0C (The manual by DANIDA ENRECA suggests T as mean in coldest month or quarter. In quarter it is 15.55) |  |  |  | 13.89
hence λ is |  |  |  | 177.8 | kg/ha/day
Hence Volume of tank(V) |  |  |  | 14060.7424 | m3
Detention time |  |  |  | 1.6873 | day
Detention time of 2 days or more is desirable to achieve sufficient BOD removal |  |  |  | 2 | day
Hence Volume of each tank (V) |  |  |  | 16666.6667 | m3
Hence Volumetric BOD loading(λ) is |  |  |  | 150 | gm/m3/day
BOD removal efficiency(in %)=2T+20 |  |  |  | 47.78 | %
For liquid depth |  |  |  | 4 | mtr.
Area at mid depth |  |  |  | 4166.6667 | m2
Length shall be L=2B
Hence mid depth width B=(area/2)1/2 |  |  |  | 45.6435 | mtr.
Hence mid length L- |  |  |  | 91.2871 | mtr.
Side slope of pond is 1V :2.5 H |  |  |  | 2.5 | mtr.
Depth for Sludge |  |  |  | 1 | mtr.
bottom below Mid depth |  |  |  | 2.5 | mtr.
Free Board |  |  |  | 1 | mtr.
Top of embankment above mid depth |  |  |  | 3.5
Hence total top length(L) |  |  |  | 108.7871 | mtr.
Hence total top width(W) |  |  |  | 63.1435 | mtr.
Area at top |  |  |  | 6869.2029 | m2
Hence total bottom length (L) |  |  |  | 78.7871 | mtr.
Hence total bottom width(W) |  |  |  | 33.1435 | mtr.
Area at Bottom |  |  |  | 2611.2837 | m2
Provide three anaerobic pond each of 108.8mx63.1m at top surface and 78.8mx33.1 m surface at bottom
DESIGN OF FACULTATIVE POND
Nomber of Tanks |  |  |  | 2 | No
Average flow in each tank |  |  |  | 12500 | cum/sec
BOD enter at Facultative pond after 2 days detention period at anaerobic pond |  |  |  | 156.66 | mg/l
Minimum mean monthly temperature 0c |  |  |  | 13.89
Volumetric BoD loading:-
λs=350 x(1.107-0.002T)(T-20) this value of BOD loading rate recommended as MEAFNRCD( Refer DANIDA) |  |  |  | 219.6676 | kg/ha/day
λs=60(1.099)^T (Refer Jodhpur design) |  |  |  | 222.6431
λs=20 T-120 |  |  |  | 157.8
λs=20T-60 |  |  |  | 217.8
λs=375-6.25L, where L-latitude(28.73), Refer manual |  |  |  | 195.4375 | kg/ha/day
Correction for above MSL=(1+(3 x10-5)xE)
where E is elevation in meters= |  |  | 210 | 1.0063
then λs is |  |  |  | 194.214 | kg/ha/day
Influent BOD to facultative pond |  |  |  | 156.66 | mg/l
value of λs is considered recommended as MEAFNRCD |  |  |  | 219.6676 | kg/ha/day
From equation (as per world bank paper) facultative mid depth area can be calculated as(A)
A=10 x Li x Q/λs
A-facultative area at mid depth in m2
Li-influent BOD concentration in mg/l, Li is BOD to be removed
Effluent to be used for restricted irrigation as such 100 effluent BOD is ok however on safe side design for effluent BOD of |  |  |  | 75
Li= |  |  |  | 81.66
then A is |  |  |  | 85356.2322 | M2
Divide the area in two ponds(area of each facultative pond) at middle of tank |  |  |  | 42678.1161 | M2
Take L=2B
Then width B=(A/2)1/2 |  |  |  | 146.0789 | M
Then L is at mid depth |  |  |  | 292.1579 | M
Hence area at mid depth is |  |  |  | 42678.1161 | M2
Adopt liquid depth |  |  |  | 1 | m
Adopt depth for sludge |  |  |  | 0.5 | m
Adopt Free Board |  |  |  | 1 | m
Total Depth of tank |  |  |  | 2.5
Area at bottom embankment slope H/V |  |  |  | 2.5
Length at bottom |  |  |  | 285.9079 | m
width at bottom |  |  |  | 139.8289 | m
Hence area at bottom is - |  |  |  | 39978.1984 | m2
Length at top including 1.0 mt free board |  |  |  | 298.4079 | m
width at top including 1.0 mt free board |  |  |  | 152.3289 | m
Area at top including 1.0 mtr free board- |  |  |  | 45456.1588 | m2
Volume of pond V=h/6(S0+4S1+S2)
h-height(liquid depth) |  |  |  | 1.5 | m
S0-area at top |  |  |  | 45456.1588 | m2
S1-area at mid water depth |  |  |  | 42678.1161 | m2
S2-area at bottom |  |  |  | 39978.1984 | m2
Hence V of each tank is |  |  |  | 64036.7054 | m3
Then detention time of each tank is |  |  |  | 5.1229 | days
Total detention time of anaerobic + facultative pond is |  |  |  | 7.1229 | days
Total area of ll afacultative ponds at top |  |  |  | 90912.3176 | m2
Total area of all anaerobic ponds at top |  |  |  | 20607.6086 | m2
Total area |  |  |  | 111519.9262 | m2
Assuming footprint area of units as % of total area |  |  |  | 60% | %
Hence total area is- |  |  |  | 185866.5437 | sqm
Hence total area in hectare taken as |  |  |  | 18.5867 | hactare
19
Total BOD removal in facultative pond |  |  |  | 81.66 | mg/l
Hence Effluent BOD is |  |  |  | 75 | mg/l
Sludge Storage andCleaning requirement
Population equivalent at 108 LPCD waste |  |  |  | 231481.4815
For anaerobic pond sludge volume |  |  |  | 0.04 | cum per capita/year
For anaerobic pond sludge volume |  |  |  | 9259.2593 | cum/year
Sludge volume provided in all anaerobic ponds |  |  |  | 8692.0808 | cum
Cleaning required period |  |  |  | 1.0653 | years
say |  |  |  | 1.0653 | years
Distribution tank for Anaerobic Pond
Consider one anerobic pond not working,
Flow height above weir, H ,Q=(2/3)*Cd*L*H^1.5*((2g)^.5),Cd=.6,L=1.2
Q per tank |  |  |  | 0.32552 | cum/sec
Assume weir length |  |  |  | 1.5 | m
H |  |  |  | 0.2441 | m
Allow free fall of |  |  |  | 0.1 | m
Total Head loss |  |  |  | 0.3441 | m
Free Board |  |  |  | 0.3 | m
Pipe from distribution tank to anaerobic pond inlet
Flow when one tank not working |  |  |  | 0.32552 | cum/sec
Pipe dia |  |  |  | 0.75 | m
velocity of flow |  |  |  | 0.7372 | m/sec
Length of pipe |  |  |  | 60 | m
head loss flq^2/10*d^5 |  |  |  | 0.026792 | m
entry/exit loss |  |  |  | 0.041549 | m
Total Losses |  |  |  | 0.068341 | m
Overflow Weir for Inlet to Anaerobic Pond
Flow when one tank not working |  |  |  | 0.32552 | cum/sec
Length of weir |  |  |  | 3 | m
Flow height above weir, H ,Q=(2/3)*Cd*L*H^1.5*((2g)^.5),Cd=.6 |  |  |  | 0.15342 | m
Allow free fall |  |  |  | 0.1 | m
Total Head loss |  |  |  | 0.25342 | m
Pipe from Anaerobic Pond Inlet to Anaerobic Pond
Peak Flow when one tank not working |  |  |  | 0.32552 | cum/sec
Pipe dia |  |  |  | 0.75 | m
velocity in pipe |  |  |  | 0.7372 | m/sec
Length of pipe |  |  |  | 40 | m
head loss flq^2/10*d^5 |  |  |  | 0.017861 | m
entry/exit loss |  |  |  | 0.041549 | m
Total Losses |  |  |  | 0.059411 | m
Overflow Weir for Inlet to Facultative Pond
Average flow when one tank not working |  |  |  | 0.14468 | cum/sec
Length of weir |  |  |  | 3 | m
Flow height above weir, H ,Q=(2/3)*Cd*L*H^1.5*((2g)^.5),Cd=.6 |  |  |  | 0.089106 | m
Allow free fall |  |  |  | 0.1 | m
Total Head loss |  |  |  | 0.18911 | m
Half flow from one anaerobic pond, Length of weir |  |  |  | 1.5 | m
Pipe from Facultative Pond Inlet to Facultative Pond
Average flow when one tank not working |  |  |  | 0.14468 | cum/sec
Pipe Dia |  |  |  | 0.6 | m
velocity of flow |  |  |  | 0.51195 | m/sec
Length of pipe |  |  |  | 40 | m
head loss flq^2/10*d^5 |  |  |  | 0.010767 | m
entry/exit loss |  |  |  | 0.020037 | m
Total Losses |  |  |  | 0.030804 | m
Overflow Weir for Outlet to Facultative Pond
Average flow |  |  |  | 0.14468 | cum/sec
Length of weir |  |  |  | 3 | m
Flow height above weir, H ,Q=(2/3)*Cd*L*H^1.5*((2g)^.5),Cd=.6 |  |  |  | 0.089106 | m
Allow free fall |  |  |  | 0.1 | m
Total Head loss |  |  |  | 0.18911 | m
Pipe from Facultative Pond outlet to Outlet Chamber 1
Average flow |  |  |  | 0.14468 | cum/sec
Assume pipe dia |  |  |  | 0.6 | m
velocity of flow |  |  |  | 0.51195 | m/sec
Length of pipe |  |  |  | 40 | m
head loss flq^2/10*d^5 |  |  |  | 0.010767 | m
entry/exit loss |  |  |  | 0.020037 | m
Total Losses |  |  |  | 0.030804 | m
Pipe from outlet Chamber 1to outlet Chamber 2
Flow |  |  |  | 0.14468 | cum/sec
Assume pipe dia |  |  |  | 0.6 | m
velocity of flow |  |  |  | 0.51195 | m/sec
Length of pipe |  |  |  | 40 | m
head loss flq^2/10*d^5 |  |  |  | 0.010767 | m
entry/exit loss |  |  |  | 0.020037 | m
Total Losses |  |  |  | 0.030804 | m
Pipe from Outlet Chamber 2 to Sewage Pump House
Flow |  |  |  | 0.28935 | cum/sec
Pipe dia |  |  |  | 0.8 | m
velocity |  |  |  | 0.57594
Length of pipe |  |  |  | 160 | m
head loss flq^2/10*d^5 |  |  |  | 0.040881 | m
entry/exit loss |  |  |  | 0.02536 | m
Total Losses |  |  |  | 0.066241 | m
Alternately Provide channal
Velocity |  |  |  | 1 | m/sec
Area |  |  |  | 0.28935 | sqm
Taking, Width=2*Height, H= |  |  |  | 0.38036 | m
Width |  |  |  | 0.76073 | m
Slope required, V=1/n*R^.67*S*.5, n=0.013, S= |  |  |  | 9.0026e-05
say |  |  |  | 0.090026 | in 1000
Sewage pumping for Irrigation and Disposal
Flow |  |  |  | 0.28935 | cum/sec
Flow in LPS |  |  |  | 289.3519 | LPS
say |  |  |  | 290 | LPS
Head |  |  |  | 15 | m
Pump working |  |  |  | 2 | No
Pump stand bye |  |  |  | 2 | No
Flow in each pump |  |  |  | 145 | lps
pump efficiency |  |  |  | 60 | %
Pump KW |  |  |  | 35.5392 | KW
Motor KW |  |  |  | 39.0931
Say |  |  |  | 40
Total No of pumps working + stand by |  |  |  | 4
Delivery Pipe velocity |  |  |  | 0.75 | m/sec
Pipe Area for combined flow of two pumps |  |  |  | 0.38667 | sqm
Pipe dia |  |  |  | 0.70183 | m
Say |  |  |  | 750 | mm
Pipe dia of delivery for each pump, velocity |  |  |  | 2.25 | m/sec
Pipe Dia |  |  |  | 0.28652 | m
Say |  |  |  | 300 | mm
Suction Pipe dia |  |  |  | 250 | mm
Sump for Effluent pumping station
flow |  |  |  | 25 | MLD
Sump storage |  |  |  | 30 | minutes
Sump Capacity |  |  |  | 520.8333 | cum
Sump depth |  |  |  | 4 | m
Sump Dia |  |  |  | 12.8791 | m
Provide Sump Dia |  |  |  | 13 | m
Sump Capacity Provided |  |  |  | 530.66 | cum
Free Board
F=(log10 A)^.5-1, F= |  |  |  | 1.1581
Wave height,H, (g*H)/V^2=.0026((gFe/V^2)^0.47, Fe is fetch,V is wind velocity, H= |  |  |  | 0.063361
Faecal Coliform Removal
Ne/Ni=1/(1+ktθa)(1+Ktθf), Ni=5*10^7, Ne= |  |  |  | 2798412.9457
Kt=2.6(1.19)^(T-20), T=13.89, kt= |  |  |  | 0.89822
Helminth Removal
R % removal=100(1-0.14 Exp(-0.38θ)) |  |  |  | 99.3303 | %
R % removal as per the table in book by DANIDA |  |  |  | 98.6 | %