## Design of STP
Design of Sewage Treatment Plant |  | for | Hapur | Extended Aeration Process
| Capacity: Average Flow | 25 | MLD
Guidance:Yellow cells are input information to be suitably filled. Green cells are to be reviewed and modified/updated.
S No | Description of Parameter | Value | Unit | Reference
| Quantity of Sewage Generated | 25000000 | Lpd
|  | 25 | MLD
|  | 25000 | Cum/day
Raw Sewage Characteristics
1 | Average Sewage flow entering the treatment plant | 25000000 | lpd
| Assumed Peak Factor | 2.25
2 | Peak Sewage flow entering the treatment plant | 56250000 | lpd
3 | COD | 400 - 800 | mg/Lt
4 | BOD | 300 | mg/Lt
5 | TDS | 1520-1620 | mg/Lt
6 | TSS | 460 | mg/Lt
7 | pH | 6.5
1 | Inlet Chamber
| Quantity of Flow (Ave) | 25000 | Cum/day
| Peak Flow | 56250 | Cum/day
|  | 0.65104 | Cum/Sec
| Assumed Detention period | 10 | sec
| Volume of the Inlet Chamber | 6.5104 | Cum
| Assumed Depth of flow | 0.6 | m
| Area Required for Inlet Chamber | 10.8507 | Sq.m
| Assumed Length to Breadth Ratio | 1
| Breadth of the Tank | 3.3 | m
| length of the Tank | 3.3 | m
Provide the Dimension of Inlet Chamber as 3.3 m x 3.3 m x 0.6 m SWD + 0.3 m Freeboard
2 | Screen Chamber (Fine Screens)
| Peak Design Flow | 0.65104 | Cum/s | Assume Size of the screen flats of size having a thickness of 10 mm and a width of 50 mm (CPHEEO page no 201)
| Assume Clear spacing between bars, o | 6 | mm | 20-50mm, pg.201 of CPHEEO Manual
| Velocity ahead of screen (Va) | 0.6 | m/sec | pg. 202 of CPHEEO Manual
| Area of Screen Channel, A= (Q/Va) | 1.09 | m2
| Keeping Side Water Depth | 0.5 | m
| Width of each screen channel, W | 2.2 | m
| Water depth upstream, ha = A/W | 0.49545 | m
| t | 0.01 | m
| Number of openings in chamber, W = X.o + (X - 1).t where , X = No. of Opening ; o = Clear Space between bars ; t = Thickness of flat | 138 | no
| Total width of opening, Ws =x*o | 0.828 | m
| Assume Angle of inclination | 60 | Degree
| Assumed Detention Period in the Screen channel | 6 | sec
| Assume Length of the screen chamber | 3.6 | m
| Inclined height of the screen, H1 | 0.572 | m
say
| Velocity through the screen, Vs= Q/H1*Ws | 1.37 | m/sec
| Head loss thru screen in normal condition, h1=0.0729(Vs2-Va2) | 0.11 | m | less than 0.15 m hence ok
| Head loss on 50% clogging h1=0.0729(2*Vs2-Va2) | 0.25 | m | less than 0.3 m hence ok
| Water Depth downstream Hb, (Za-Zb)+Va2/2g-Vs2/2g+Ha-Headloss thru screen in normal condition | 0.31 | m
| Water Depth downstream Hb, (Za-Zb)+Va2/2g-Vs2/2g+Ha-Headloss thru screen in clogged condition | 0.17 | m
Provide the Dimension of Screen Chamber (Fine Screens) as 3.6 m x 2.2 m x 0.5 m SWD + 0.3 m Freeboard
3 | Grit Removal unit
| No. of Grit channels | 2 |  | (1W+1SB)
Computation of Settling Velocity: Stoke's Law
| Kinematic Viscosity of Effluent assumed | 1.1e-06 | sqm/sec
| Particle Diameter assumed | 0.00015 | m
| Settling Velocity | 0.02 | m/s | Pg,208,209 of CPHEEO manual
| Reynold's number, Re=(d.Vs/Kinematic viscosity) | 2.73
| for Transition flows, Vs=[(0.707(Ss-1)d1.6v-0.6)]0.714 | 0.017061 | m/s | Pg,208,209 of CPHEEO manual
| Actual Setling velocity | 0.017061 | m/s | Pg,208,209 of CPHEEO manual
| removal efficiency | 1474.07 | cum/sqm/d
| Assumed Removal Efficiency | 75 | %
|  | 1105.5525 | cum/sqm/d
| Actual Surface Over Flow Rate :(Q/A)= Vsn/[(1-η)-0.125-1] | 973.8438 | cum/sqm/d | Pg 209-take n=.125, as per table 11.1-it is 1555
Dimensions of grit channel:
| Peak Flow | 56250 | cum/day
| Total Plan area of Grit channel = Qpeak/(Q/A) | 57.76 | m2
| Assumed Width of the Grit channel | 2.5 | m
| Length of the Channel | 23.1 | m
| Liquid Depth assumed | 1.5 | m
| Provide a depth for the Grit Storage | 0.3 | m
Provide the Dimension of Grit Removal unit as 23.1 m x 2.5 m x 1.5 m SWD + 0.3 m Freeboard
Mechanical Grit Removal Unit
| Square Type Grit Removal Tank with Grit Hopper | 7.6 | m
Provide Mehcnical Grit Chamber with Grit lift Pumps having a size of 7.6 m* 7.6 m and 1.5 m SWD + 0.3 m Freeboard
4 | Parshall flume |  |  | (Optional)
| Width of grit chamber | 2.5 | m
| Throat width of flume (W) | 0.3 | m | table 11.2, 211 cph
| Sloping convergent length towards throat (A) | 1.35 | m | table 11.2, 211 cph
| Width at the beginning of convergent section (D) | 0.831 | m | table 11.2, 211 cph
| Length of convergent section (B) | 1.322 | m | table 11.2, 211 cph
| Far end Width of divergent section (G) | 0.9 | m | table 11.2, 211 cph
| Length of divergent section (C) | 0.6 | m | table 11.2, 211 cph
| Length of the throat (F) | 0.6 | m | table 11.2, 211 cph
| K | 0.075 | m | table 11.2, 211 cph
| Z, - Constant | 0.38 | m | table 11.2, 211 cph
| Free board | 0.25 | m
Calculations & Dimensions
| Q, MLD | Q, lps | D, m | C/s area, m2 | V, m/s
| 30 | 347.2222 | 0.32172 | 0.80429 | 0.43171 | Q, min
| 60 | 694.4444 | 0.73648 | 1.8412 | 0.37717
| 90 | 1041.6667 | 1.085 | 2.7125 | 0.38403
| 120 | 1388.8889 | 1.3964 | 3.491 | 0.39785
| 150 | 1736.1111 | 1.6829 | 4.2072 | 0.41266 | Q, max
Note: The variation of velocity is within the permissible 10% deviation. Hence the section provided is OK
Note: Check for B =1.5 *Qmax^0.33 and not less than the value given in table (adopted value)
D as per formula 11.18 page 212 of Manual, V as per 11.21
5 | Equalization Tank (Collection Chamber )
| Peak Design Flow | 56250 | Cum/day
| Assumed Detention period | 2.1 | hours
| Volume of the Tank | 4921.875 | Cum
| Assumed Depth of Liquid column | 2.5 | m
| Area required for the equalization tank | 1968.75 | Sq.m
| No. of Tanks Proposed | 2
| area required for each equalization tank | 984.375 | Sq.m
| Length to Breadth ratio | 1
| Breadth of the tank | 31.5 | m
| Length of the tank | 31.5 | m
Provide the Dimension of Equalization Tank (Collection Chamber ) as 31.5 m x 31.5 m x 2.5 m SWD + 0.3 m Freeboard
Mixing Arrangements
| Assumed BOD reduction in the tank | 15% | Percent
| Incoming BOD of Raw sewage | 300 | mg/L
| BOD to be reduced | 45 | mg/L
| BOD Load | 2531.25 | kg/day
| Oxygen required to remove BOD load | 2 | kg/kg of BOD
| Oxygen required | 5062.5 | kg/day
|  | 210.9375 | kg/hr
| Actual Air Required | 13286.5646 | Cum/hr
| Provide Corse bubble aeration grids for | 13290 | cum/hr
6 | Raw Sewage Pumps
No. of pumps - 2 (2W+2SB)
Type of Pumps - Submersible/Horizontal Centrifugal
| Average flow | 25000 | Cum/day
| Number of working hours | 20 | hrs
| Flow Capacity of Pump required | 1250 | Cum/hr
| Proposed pumps 4numbers (2W + 2SB), flow per Pump | 625 | Cum/hr
|  | 173.6111 | lps
| Head required | 14 | m
| HP required for pump | 65 | hp
7 | Aeration tank
| No of Tanks | 2
Flow - completely mixed
| Q- per tank | 12500 | cum/day
| BOD | 255 | mg/Lt
| MLSS | 2500
Type Aeration - Diffuser type fine bubble
| Blowers - | 2 |  | ( 1W+1SB)
| F/M assumed | 0.12
| Volume of the tank | 10625 | Cum | volume of tank as per 13.6 page 226
| Add additional volume of 25% for sludge recycle | 2656.25 | Cum
| Total volume of tank | 13281.25 | Cum
| Hydraulic Detention Time | 1.0625 | day
| Depth of the tank | 4 | m
| Area of the Tank | 3320.3125 | Sq.m
| Area for each tank | 3320.3125 | Sq.m
| Assumed Breadth to Length Ratio | 1
| width of the tank | 57.7 | m
| Length of tank | 57.6 | m
Provide the Dimension of Aeration tank as 57.6 m x 57.7 m x 4 m SWD + 0.5 m Freeboard
8 | Blower capacity
| BoD load | 3187.5 | kg/day
|  | 132.8125 | kg/hr
| Oxygen Required for 1 kg BOD removal | 2 | kg
| Theoretical Oxygen | 265.625 | kg/hr
| Actual requirement of air | 12548.4221 | cum/hr
| Total Air Requirement | 25835 | Cum/hr
| fine bubble diffuser assumed to inject oxygen of | 10 | cum/hr
| Provide Membrance diffuser for aeration tank | 2583.5 | No.
| Provide 2 Blowers of capacity at 0.45 ksc (1W+ 1 SB) | 25835 | cum/hr | for each tank
| Sludge Volume Index assumed | 100 |  | Page 235-SVI 80 to 150
| Sludge Recirculation Qr/Q=Xt/((10^6/SVI)-Xt) | 0.33333 |  | table 13.1 page 235 or taking SVI 100
| Volumetric loading rate | 0.24 | kg/cum
| Xt V = | 26562500
| ay Q (Yo – Ye) qc/(1 + ke qc) | 2937500 |  | equation 13.7 page 227
0.11059
0.050588
| Hydraulic Mean Cell Residence Time | 19.7674 | days
| Assumed Reduction in the Aeration Tank | 95 | %
| Outlet BOD from the Aeration tank | 12.75 | mg/L
9 | Secondary clarifier
| No. of Tanks | 2
| Average Flow in each tank | 12500 | cum/day
| SOR | 25 | Cum/Sqm/day | Table 12.1, but it is 8-15 for average flow and 25-35 for peak flow for extended aeration
| SWD | 2 | m | table 12.1, it is 3.5-4.5 m for extended aeration, although para 12.4.2.5 give depth 2 m in vertical flow tanks
| Solid conc. In settled sludge -% | 0.8 to 0.9 | %
Withdrawal frequency - continuous
| Area Required for the Tank | 500 | Sq.m
| Diametre Required for Secondary Settling Tank | 25.2313 | m
| Assumed Detention Period | 3.1 | hrs | 1.5-2 hrs as per table 12.1
|  | 1614.5833 | Cum
| Depth of the Clarifier assumed | 2.5 | m
| Area of the Clarifier | 645.8333 | Sq.m
| Provide Secondary Clarifier of Diametre | 28.7 | m | OK.
| Surface Loading Rate | 19.3548 | Cum/Sq.m/day
Provide the Dimension of Secondary clarifier as 28.7 m diamtre x 2.5 m SWD + 0.5 m Freeboard
| Assumed BOD reduction in Clarifier | 20 | %
| Outlet BOD from Clarifier | 10.2 | mg/L
10 | Return Activated Sludge /Excess sludge pumps
Type of Pumps - Centrifugal
| No. of pumps | 4 |  | (2W+2SB)
| Assumed return flow | 50 | %
| Return sludge Pumps | 6250 | Cum/day
| Operating hours | 20
| Capacity of pump required | 312.5 | Cum/hr
|  | 86.8056 | lps
| Head required | 8 | m
| Power requirement for the Pump | 19 | Hp
10 | Treated Sewage Sump
| Assumed Detention time | 15 | Minutes
| Average Flow | 25000 | Cum/day
| Volume of the tank | 260.4167 | Cum
| Provide a depth of tank as | 4 | m
| Area of the Tank | 65.1042 | Sq.m
| Square tank Size | 8.1 | m
Provide the Dimension of Treated Sewage Sump as 8.1 m x 8.1 m x 4 m SWD + 0.3 m Freeboard
11 | Pressure Sand Filter
| Average Flow | 25000 | Cum/day
| Filter Operating hours | 20 | hrs
| Operating flow | 1250 | Cum/hr
| Filter Loading rate | 11 | Cum/hr/Sq.m
| Area of the Filter required | 113.6364 | Sq.m
| Diameter of the Filter Required | 12.1 | m |  |  | 13.52
| Provide the Dimension of Pressure Sand Filter as 12.1 m x Diametre with 1.8 m Shell height |  |  |  |  | 13.5
12 | Filter feed Pumps
| Provide Filter feed pumps of capcity | 1250 | Cum/hr
|  | 15 | head
Chlorine Mixing
| Reduction in BOD Expected in Dual media filter | 20 | % |  |  | Average Flow | 25000 | Cum/day
| Exit BOD from the Dual media filter | 8.16 | mg/L |  |  | Chlorine Dosing Rate | 0.8 | mg/L
[6 empty] | Percentage of Chlorine in Bleaching powder | 25
13 | Disinfection through Chlorination |  |  |  |  | Density of solution | 1 | gm/ml
| Bleaching powder Dozers, 1W+1SB | 3500 | litres/hour |  |  | Strength of the solution | 1 | %
| or Vacuum Chlorinater 1 W+1 SB | 1 | Kg/hour
| Chlorine Contact tank 15 minute detention | 8.1*8.1*4 | m*m*m |  |  | Bleaching powder required | 80 | kg/d
14 | Filter press for Sludge Disposal to handle sludge of | 15000 | kg/day |  |  | for one percent solution, tank capacity, | 8000 | liter
|  | 1428571.4286 | Cum/day |  |  | Dosing Rate | 80000000 | ml/day
|  | 11904.7619 | Cum/hr |  |  |  | 80000 | l/day
[7 empty] | 3333.3333 | lph
| Or |  |  |  |  | Say | 3333.3333 | lph
| Population Equivalent | 187500 | Persons |  |  | Volume of the tank required per shift of 8 hours | 26.6667 | cum
| area per person | 0.025 | Sq.m |  |  | Provide 2W+1SB, Capacity of each tank | 13.3333
| Total Area required | 4687.5 | Sq.m | 5120
| Provide Sludge Drying Beds of Size 16 m x 16 m x 1.8 M TD - 20 No. |  |  |  |  | Provide a tank size of3.0m x 3.0m x(1.5m +.3m )TD
| Pipe Sizes (Diameter in mm) |  |  |  |  | BOD reduction after Disinfection | 10 | %
[6 empty] | BOD outlet to Garden or Reuse for Flushing is | 7.344 | Mg/L
Gravity Lines
| Sludge line | 160 | mm
| Sewage line | 125 | mm
15 | Pump House
| Size of the Pump House | 100 | Sq.m
Hydraulic Calculations
| Average Ground Level | 210 | m
Inlet Chamber
| Water Level in the Inlet Chamber be | 212 | m
| Liquid Depth Provided in the Inlet Chamber | 0.6 | m
| Bed Level of Inlet Chamber | 211.4 | m
Bar Screen Chamber
| Water Level in the Bar Screen Chamber be | 211.35 | m
| Bed Level of U/s of Bar Screen Chamber | 211.04 | m
| Bed Level of D/s of Bar Screen Chamber | 210.79 | m
Grit Chamber
| Water Level in the Grit Chamber be | 210.69 | m
| Bottom Level of Grit Chamber | 209.19 | m
| Silt Depoition Hopper bottom level | 208.89 | m
Equalization Tank
| Water Level in the Equalization tank | 210.19 | m
| Bed Level of Equalization tank | 207.69 | m
Aeration Tank
| Water Level in the Aeration Tank | 209.79 | m
| Bed Level of Aeration Tank | 205.79 | m
Secondary Clarifier
| Water Level in the Secondary Clarifier | 209.39 | m
| Bottom Level of secondary Clarifier | 206.89 | m
Treated Sewage Sump
| Water Level in the Sump | 208.39 | m
| Bed Level of Treated Sewage Sump | 204.29 | m
| Wall Top Level of Treated Sewage Sump | 210.5 | m
Pump House
| Size of the Pump House | 100 | Sq.m
| Finished Floor Level of the Pump House above Treated Sewage Sump | 210.65 | m
| Roof Bottom Level of Pump house | 214 | m