## Sam Design rising Main
Design of Raw (or Clear) Water Main
Guidance Note: the data in yellow cell to be suitably filled | [5 empty] | From: | Yamuna River | To: | WTP | Panipat
1) Water requirement : |  |  |  | Year | Peak Discharge |  | Pipe Dia in mm | Material | Class | HWC | Rate Rs/m
A. | Initial |  |  | 2011 | 62.02 | mld | 250 | DI | K7 | 140 | 2005
B. | Intermediate |  |  | 2026 | 83.85 | mld | 300 | DI | K7 | 140 | 2543
C. | Ultimate |  |  | 2041 | 105 | mld | 350 | DI | K7 | 140 | 3197
2) Pumping main |  |  |  | LENGTH | 19000 | M | 400 | DI | K7 | 140 | 3833
3) Static head for pump |  |  |  | ST.HEAD | 11 | M | 450 | DI | K7 | 140 | 4547
4) Design period |  |  |  | YEAR | 30 | yr. | 500 | DI | K7 | 140 | 5325
5) Combined eff. of pump set |  |  |  | EFF. % | 75 | % | 600 | DI | K7 | 140 | 7015
6) Cost of pumping unit |  |  |  | Rs./KW | 25000 | Rs | 700 | DI | K7 | 140 | 9622
7) Interest rate |  |  |  | INTEREST | 10 | % | 800 | DI | K7 | 140 | 12550
8) Life of electric motor & pump set |  |  |  | P.Yrs | 15 | yr. | 900 | DI | K7 | 140 | 15314
9) Energy charges per kWh |  |  |  | P/KWH | 475 | paise | 1000 | DI | K7 | 140 | 18354
10) Pumping hours for discharge at the end of 15 years |  |  |  | hours | 23 | hrs | 1100 | DI | K7 | 140 | 21600
CALCULATIONS: |  |  |  |  | 1st 15 years |  | 2nd 15 years
1) Discharge at Start OF PERIOD |  |  |  |  | 62.02 | mld | 83.85 | mld
2) Discharge at the end of 15 yrs |  |  |  |  | 83.85 | mld | 105 | mld
3) Average Flow |  |  |  |  | 880.8575 | lps | 1140.3986 | lps
4) Average Discharge |  |  |  |  | 72.935 | mld | 94.425 | mld
5) Avg.pumping hours during the period |  |  |  |  | 20.006 | hrs | 20.6836 | hrs
6) KW required at combined efficiency of pumping set |  |  |  |  | 12.0151 | * H1 | 15.5553 | * H2
7) annual charges for energy Rs. |  |  |  |  | 417034.7183 | * KW1 | 558197.6348 | * KW2
Modified Hazen William's Formula
|  |  |  | V= | 143.534CR r0.6575 S0.5525
|  |  |  | h= | [L(Q/CR)1.81 ]/[994.62D4.81]
Friction Head Loss (First 15 years)
Dia. in mm | L | Q | CR | Q/CR | (Q/CR)1.81 | 994.62 | D | D4.81 | h( First 15 yrs)
250mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.25 | 0.0012708 | 628.8262
300mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.3 | 0.0030546 | 261.6187
350mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.35 | 0.0064116 | 124.6392
400mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.4 | 0.012187 | 65.5713
450mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.45 | 0.021476 | 37.2109
500mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.5 | 0.035649 | 22.4169
600mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.6 | 0.085686 | 9.3264
700mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.7 | 0.17985 | 4.4432
800mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.8 | 0.34187 | 2.3375
900mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 0.9 | 0.60243 | 1.3265
1000mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 1 | 1 | 0.79914
1100 mm | 1000 | 0.88086 | 1 | 0.88086 | 0.79484 | 994.62 | 1.1 | 1.5816 | 0.50527
Velocity
Dia. in mm | 143.534 | CR | r=A/P=D/4 | r0.6575 | S | S0.5525 | V
250 | 143.534 | 1 | 0.0625 | 0.16154 | 0.62883 | 0.77391 | 17.9446
300 | 143.534 | 1 | 0.075 | 0.18212 | 0.26162 | 0.47672 | 12.4615
350 | 143.534 | 1 | 0.0875 | 0.20154 | 0.12464 | 0.31648 | 9.1553
400 | 143.534 | 1 | 0.1 | 0.22004 | 0.065571 | 0.22194 | 7.0095
450 | 143.534 | 1 | 0.1125 | 0.23776 | 0.037211 | 0.16229 | 5.5384
500 | 143.534 | 1 | 0.125 | 0.25481 | 0.022417 | 0.12266 | 4.4861
600 | 143.534 | 1 | 0.15 | 0.28726 | 0.0093264 | 0.075556 | 3.1153
700 | 143.534 | 1 | 0.175 | 0.31791 | 0.0044432 | 0.05016 | 2.2888
800 | 143.534 | 1 | 0.2 | 0.34708 | 0.0023375 | 0.035175 | 1.7524
900 | 143.534 | 1 | 0.225 | 0.37502 | 0.0013265 | 0.025722 | 1.3846
1000 | 143.534 | 1 | 0.25 | 0.40193 | 0.00079914 | 0.01944 | 1.1215
1100 | 143.534 | 1 | 0.275 | 0.42792 | 0.00050527 | 0.01509 | 0.92686
Friction Head Loss (Second 15 years)
Dia. in mm | L | Q | CR | Q/CR | (Q/CR)1.81 | 994.62 | D | D4.81 | h( Second 15 yrs)
250mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.25 | 0.0012708 | 1003.5151
300mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.3 | 0.0030546 | 417.5054
350mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.35 | 0.0064116 | 198.9061
400mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.4 | 0.012187 | 104.6422
450mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.45 | 0.021476 | 59.3831
500mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.5 | 0.035649 | 35.7742
600mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.6 | 0.085686 | 14.8836
700mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.7 | 0.17985 | 7.0908
800mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.8 | 0.34187 | 3.7304
900mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 0.9 | 0.60243 | 2.1169
1000mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 1 | 1 | 1.2753
1100 mm | 1000 | 1.1404 | 1 | 1.1404 | 1.2684 | 994.62 | 1.1 | 1.5816 | 0.80634
Velocity
Dia. in mm | 143.534 | CR | r=A/P=D/4 | r0.6575 | S | S0.5525 | V
250 | 143.534 | 1 | 0.0625 | 0.16154 | 1.0035 | 1.0019 | 23.2321
300 | 143.534 | 1 | 0.075 | 0.18212 | 0.41751 | 0.61719 | 16.1333
350 | 143.534 | 1 | 0.0875 | 0.20154 | 0.19891 | 0.40973 | 11.853
400 | 143.534 | 1 | 0.1 | 0.22004 | 0.10464 | 0.28733 | 9.0749
450 | 143.534 | 1 | 0.1125 | 0.23776 | 0.059383 | 0.21011 | 7.1703
500 | 143.534 | 1 | 0.125 | 0.25481 | 0.035774 | 0.1588 | 5.8079
600 | 143.534 | 1 | 0.15 | 0.28726 | 0.014884 | 0.097819 | 4.0333
700 | 143.534 | 1 | 0.175 | 0.31791 | 0.0070908 | 0.064939 | 2.9632
800 | 143.534 | 1 | 0.2 | 0.34708 | 0.0037304 | 0.04554 | 2.2687
900 | 143.534 | 1 | 0.225 | 0.37502 | 0.0021169 | 0.033301 | 1.7925
1000 | 143.534 | 1 | 0.25 | 0.40193 | 0.0012753 | 0.025168 | 1.452
1100 | 143.534 | 1 | 0.275 | 0.42792 | 0.00080634 | 0.019537 | 1.2
TABLE 1 - VELOCITY AND HEADLOSSES FOR DIFFERENT PIPE SIZES
S No | Pipe Size in mm | friction head loss per 1000 m |  | Velocity in m/sec | Velocity in m/sec | Friction head loss | other losses at 10% | total losses (H1) including static head | Friction head loss in total pipe length | other losses at 10% | total losses (H2) including static head
|  | 1st stage flow | 2nd stage flow | 1st stage flow | 2nd stage flow | 1st stage flow |  | 11 | 19000 |  | 11
2nd stage flow
1 | 250 | 628.8262 | 1003.5151 | 17.9446 | 23.2321 | 11947.697 | 1194.7697 | 13142.4667 | 19066.7872 | 1906.6787 | 20973.4659
2 | 300 | 261.6187 | 417.5054 | 12.4615 | 16.1333 | 4970.7555 | 497.0756 | 5467.8311 | 7932.6031 | 793.2603 | 8725.8634
3 | 350 | 124.6392 | 198.9061 | 9.1553 | 11.853 | 2368.1453 | 236.8145 | 2604.9598 | 3779.2156 | 377.9216 | 4157.1372
4 | 400 | 65.5713 | 104.6422 | 7.0095 | 9.0749 | 1245.8538 | 124.5854 | 1370.4392 | 1988.2015 | 198.8202 | 2187.0217
5 | 450 | 37.2109 | 59.3831 | 5.5384 | 7.1703 | 707.0066 | 70.7007 | 777.7072 | 1128.2797 | 112.828 | 1241.1077
6 | 500 | 22.4169 | 35.7742 | 4.4861 | 5.8079 | 425.9218 | 42.5922 | 468.514 | 679.7093 | 67.9709 | 747.6803
7 | 600 | 9.3264 | 14.8836 | 3.1153 | 4.0333 | 177.2018 | 17.7202 | 194.922 | 282.7883 | 28.2788 | 311.0671
8 | 700 | 4.4432 | 7.0908 | 2.2888 | 2.9632 | 84.4217 | 8.4422 | 92.8639 | 134.7248 | 13.4725 | 148.1972
9 | 800 | 2.3375 | 3.7304 | 1.7524 | 2.2687 | 44.4133 | 4.4413 | 48.8546 | 70.8771 | 7.0877 | 77.9648
10 | 900 | 1.3265 | 2.1169 | 1.3846 | 1.7925 | 25.204 | 2.5204 | 27.7244 | 40.2219 | 4.0222 | 44.2441
11 | 1000 | 0.79914 | 1.2753 | 1.1215 | 1.452 | 15.1836 | 1.5184 | 16.702 | 24.2309 | 2.4231 | 26.654
12 | 1100 | 0.50527 | 0.80634 | 0.92686 | 1.2 | 9.6001 | 0.96001 | 10.5601 | 15.3204 | 1.532 | 16.8524
TABLE 2 - KILOWATTS & COST OF PUMP SETS REQUIRED FOR DIFFERENT PIPE SIZES AND PIPE COST
|  |  | 1st stage flow in MLD |  | 72.935 |  | 2nd stage flow in MLD |  | 94.425
S No | Pipe Dia in mm | class of Pipe | H1 total head in meters | KW reqd plus 50% stand by | pump cost at Rs per Kw |  | H2 total head in meters | Kw required plus 50% stand by | Pump cost at Rs per KW | cost of pipe per meter | total cost of pipe in thousand Rs
[9 empty] | 25000 |  | 19000
1 | 250 | K7 | 13142.4667 | 236862.2029 | 5921555.0726 |  | 20973.4659 | 489373.098 | 12234327.4509 | 2005 | 38095
2 | 300 | K7 | 5467.8311 | 98544.8586 | 2463621.4644 |  | 8725.8634 | 203600.2458 | 5090006.1455 | 2543 | 48317
3 | 350 | K7 | 2604.9598 | 46948.3045 | 1173707.6118 |  | 4157.1372 | 96998.3261 | 2424958.1535 | 3197 | 60743
4 | 400 | K7 | 1370.4392 | 24698.9589 | 617473.9726 |  | 2187.0217 | 51029.6953 | 1275742.3818 | 3833 | 60743
5 | 450 | K7 | 777.7072 | 14016.3526 | 350408.8152 |  | 1241.1077 | 28958.7187 | 723967.967 | 4547 | 86393
6 | 500 | K7 | 468.514 | 8443.869 | 211096.724 |  | 747.6803 | 17445.5961 | 436139.9014 | 5325 | 101175
7 | 600 | K7 | 194.922 | 3513.0125 | 87825.3118 |  | 311.0671 | 7258.1179 | 181452.9476 | 7015 | 133285
8 | 700 | K7 | 92.8639 | 1673.6538 | 41841.3455 |  | 148.1972 | 3457.8803 | 86447.0086 | 9622 | 182818
9 | 800 | K7 | 48.8546 | 880.4899 | 22012.247 |  | 77.9648 | 1819.1508 | 45478.7694 | 12550 | 238450
10 | 900 | K7 | 27.7244 | 499.6671 | 12491.6769 |  | 44.2441 | 1032.3455 | 25808.6371 | 15314 | 290966
11 | 1000 | K7 | 16.702 | 301.0144 | 7525.3589 |  | 26.654 | 621.9157 | 15547.893 | 18354 | 348726
12 | 1100 | K7 | 10.5601 | 190.3217 | 4758.0434 |  | 16.8524 | 393.2174 | 9830.4348 | 21600 | 410400
TABLE 3 - COMPARATIVE STATEMENT OF OVERALL COST OF PUMPING MAIN FOR DIFFERENT PIPE SIZES
| 1st stage flow |  | 72.935 | mld | 2nd stage flow |  | 94.425 | mld
S No | Cost of pump set | Annual Energy Charges | capitalized energy cost | Pump cost+capitalized energy cost | Cost of pump set | Annual Energy Charges | capitalized energy cost | Pump cost+capitalized energy cost | Present cost of pump and capitalized cost of 2nd stage | Pipe Dia | Grand total cost first and second stage
| Thousand Rs | Thousand Rs | Thousand Rs | Thousand Rs | Thousand Rs | Thousand Rs | Thousand Rs | Thousand Rs | Thousand Rs | mm | Thousand Rs
1 | 5921555.0726 | 5480864.881 | 41687458.2848 | 47609013.3574 | 12234327.4509 | 11707339.0829 | 89046021.0648 | 101280348.5157 | 24247150.71 | 250 | 71894259.0675
2 | 2463621.4644 | 2280275.4004 | 17343774.6955 | 19807396.1599 | 5090006.1455 | 4870756.3304 | 37046972.649 | 42136978.7945 | 10087857.0252 | 300 | 29943570.1852
3 | 1173707.6118 | 1086358.6932 | 8262844.2203 | 9436551.8322 | 2424958.1535 | 2320504.129 | 17649754.4051 | 20074712.5586 | 4806012.104 | 350 | 14303306.9362
4 | 617473.9726 | 571520.7187 | 4346986.5866 | 4964460.5592 | 1275742.3818 | 1220790.3301 | 9285331.2504 | 10561073.6322 | 2528387.2713 | 400 | 7553590.8305
5 | 350408.8152 | 324330.9141 | 2466860.9324 | 2817269.7477 | 723967.967 | 692783.3597 | 5269310.2336 | 5993278.2006 | 1434828.3937 | 450 | 4338491.1414
6 | 211096.724 | 195386.6184 | 1486110.6193 | 1697207.3433 | 436139.9014 | 417353.3636 | 3174389.6835 | 3610529.5849 | 864383.4295 | 500 | 2662765.7728
7 | 87825.3118 | 81289.2325 | 618285.9022 | 706111.2139 | 181452.9476 | 173636.9403 | 1320682.5681 | 1502135.5158 | 359620.6645 | 600 | 1199016.8784
8 | 41841.3455 | 38727.4556 | 294561.0274 | 336402.3729 | 86447.0086 | 82723.341 | 629193.7319 | 715640.7404 | 171328.8821 | 700 | 690549.255
9 | 22012.247 | 20374.0656 | 154965.1429 | 176977.3898 | 45478.7694 | 43519.791 | 331011.5306 | 376490.3 | 90134.1393 | 800 | 505561.5292
10 | 12491.6769 | 11562.0293 | 87940.7951 | 100432.4721 | 25808.6371 | 24696.9412 | 187844.9351 | 213653.5722 | 51150.0053 | 900 | 442548.4774
11 | 7525.3589 | 6965.3114 | 52978.1585 | 60503.5174 | 15547.893 | 14878.1742 | 113163.3928 | 128711.2858 | 30814.2892 | 1000 | 440043.8065
12 | 4758.0434 | 4403.9433 | 33496.393 | 38254.4364 | 9830.4348 | 9406.9931 | 71549.5891 | 81380.0239 | 19482.8882 | 1100 | 468137.3245
|  |  | Minimum Capitalized cost Rs |  | 440043.8065 | thousands
Optimum pipe size corresponds to minimum capitalized cost