## Sheet1
Design of Conventional water Treatment Plant
Note: i) Data in yellow cell to be suitably filled as per requirement
ii) Data in green cell to review the provided value and revise/update if required
Design Flow output from WTP | 100 | MLD
Design Flow input to WTP, consider 5% losses in WTP | 105 | MLD
Design flow | 4375 | cu/hour
Pumping Hours in Raw Water Pumping Station | 23 | Hours
On the basis of 23 hour pumping, design flow | 4565.2174 | cu/hour
Consider Inlet channel having width of | 2 | m
Consider Inlet channel having depth of | 0.8 | m
Over loading capacity | 20%
Velocity of flow in channal | 0.95109 | m/sec
Length of channel | 40 | m
Head loss across manual screen | 16 | mm
Water supply level at inlet of channal | 240.1 | m
Top Water Level downstream of screen | 240.084 | m
Hydraulic Radious of Channal (Area/Perimeter) | 0.44444 | m
Slope Friction loss per 1000 m in Channal | 0.00060159 | m
Losses in Channal | 0.024064 | m
Water Treatment Plant
Design flow | 4565.2174 | cu/hour
Inlet chamber detention time | 45 | Sec
Provide Inlet Chamber of size | 3.6*3.6*4.5 | m*m*m
Volume provided | 58.32 | cum
Detention Time provided | 45.9895 | Seconds
No of Flash Mixers and Clariflocullator | 2 | Nos
Flow in each Flash Mixer | 2282.6087 | cum/hr
Detention Time in flash mixture, range 30-60 seconds | 45 | Sec
Volume required for every flash mixture | 28.5326 | cum
Provide Diameter of Flash mixture | 3.25 | m
Required depth of Flash mixture | 3.4412 | m
Provide depth of Flash mixture | 3.5 | m
Clariflocculators
No.s | 2 | Nos
Flow in every Clariflocculator | 2282.6087 | cum/hour
Detention time in flocculation zone, range 10-40 minutes | 30 | Minutes
Volume reqd. in flocculation zone | 1141.3043 | cum
Provide Water Depth in flocculation zone, range 3-4.5 m | 3.75 | m
Required Dia of flocculation tank | 19.6902 | m
Provide Dia of flocculation tank | 20 | m
Volume provided | 1177.5 | cum
Assume surface loading (Range 35-50 m/day) | 35 | m/day
Surface area required | 1565.2174 | sqm
Area of Flocculation | 314 | sqm
Total Area of Clariflocculator including flocculation | 1879.2174 | sqm
Dia of Clariflocculator | 48.9276 | m
Provide Dia | 49 | m
Detention time (detention time range 1-2 hours), | 2 | hours
Volume required in Clarifying zone | 4565.2174 | cum
Volume required in Clarifying zone | 1178.25 × 3 = 3534.75 m3
Water depth in clarifying zone | 3 | m
Volume provided in Clarifying zone, | 4695.6522 | cum
Provide outlet launder of , width | 0.8 | m
Provide outlet launder of , depth | 0.8 | m
Flow in Launder, for 50% flow lenfth | 1141.3043 | m3/hr
Velocity of flow in launder for design flow | 0.49536 | m/sec
Weir Loading taken | 300 | m3/d/m
Launder Perimeter required | 182.6087 | m
Provide weir to have inlet from both sides, thus launder perimeter required is | 91.3043 | m
Actual launder length provided | 155.116 | m
Filters
No,s | 10 | nos
Total output | 4565.2174 | cum/hour
Rate of Filtration | 6 | m/hour
Input to each of 10 filters | 456.5217 | cum/hour
Area required for each filter | 76.087 | sqm
Provide twin bed filters section | 3.60m×10.7m*2 No
Area of each twin filter | 77.04 | Sqm
Inlet: sluice gate width | 350 | mm
Inlet: sluice gate depth | 350 | mm
Velocity | 1.0352 | m/sec
Outlet: Provide Sluice Valve dia | 350 | mm
Velocity in outlet sluice valve | 1.3187 | m/sec
Wash Water rate | 500 | lpm/m2
Wash water rate reqd | 38.52 | cum/minute
Wash water rate reqd | 0.642 | cum/sec
Provide SV dia for wash water | 800 | mm φ
Velocity | 1.2779 | m/sec
Wash out; Provide gate / width | 0.75 | m
Wash out; Provide gate / depth | 0.75 | m
Velocity | 1.1413 | m/sec
Air – inlet required rate | 750 | lpm/m2
Air flow rate | 57.78 | cum/minute
Air flow rate | 0.963 | cum/sec
sluice valve for Air inlet, dia for each filter bed | 250 | mm
Velocity | 19.628 | m/sec
Wash water Pump | 2311.2 | m³/hr
Capacity required
Provide 3 Submerssible pump sets (2W+1S), working pumps= | 2 | no working
Capacity of each pump | 1155.6 | cum/hr
Capacity of each pump | 19260 | LPS
Air blower
Air capacity reqd. | 3466.8 | cum/hour
Provide two blowers (1W + 1S) of capacity | 3500 | cum/hour
Chemical House
Consider an average of dose of alum at | 50 | ppm
strength solution | 10 | %
Solution required for 8 hrs | 18260.8696 | litres
Solution required for 8 hrs | 18.2609 | cum
Provide 3 tanks each of | 3.25×2.8×2.2 | m*m*m
Alum required for 90 days | 493043.4783 | Kg
Taking alum density | 1300 | kg/m3
Volume of alum | 379.2642 | cum
Taking stake height as , | 2 | m
Area required for alum storage | 189.6321 | sqm
Taking provision for movement and putting weighing scale etc., Provide additional storage area for Alum | 20% | %
Additional area for movement, weight scale | 37.9264 | sqm
Total Area required | 227.5585 | sqm
Total Area required | 230 | sqm