## Design Tube Settler
Design of Tube Settler
Note: Data in yellow cell to be suitably filled for particular application. Data in green cell to be reviewed and updated if need be.
Description | Value | Units
Number of Tube Settlers | 1
Design Flow | 100 | MLD
| 4347.8261 | m3/hr.
Design Flow Each | 4350 | m3/hr.
Detention in Flocculation Zone | 0.5 | hr
Detention in Clarification Zone | 0.4 | hr
Volume in Flocculation Zone | 2175 | m3
Volume in Clarification Zone | 1740 | m3
OD of Central Shaft | 1.1 | m
C/S Area of Central Shaft | 0.94985 | m2
Surface Loading Rate in Clarification Zone | 156 | m3/m2/day
Area of Clarification zone | 669.2308 | m2
SWD Clarification Zone - required | 2.6 | m
SWD Clarification Zone - provided | 3 | m
SWD Flocculation Zone - provided | 3.3 | m
Area Flocculation Zone | 659.0909 | m2
Total Area Flocculation Zone | 660.0408 | m2
Dia Flocculation Zone | 28.9968 | m
| 29 | m
Flocculator wall thickness | 0.15 | m
OD Flocculation Zone | 29.3 | m
Outer Area Flocculation Zone | 673.9147 | m2
Total Area required in Clarification zone | 1343.1454 | m2
Dia required | 41.3644 | m
Considering wastage of space due to inclined tube settler, say | 42 | m
Launder width | 0.6 | m
Launder wall thickness | 0.1 | m
Approx Launder Area | 107.5136 | m2
Area incl launder required | 1492.2536 | m2
Dia required | 43.4 | m
say | 43.4 | m
Free Board | 0.3 | m
Bottom Slope | 1 in 12
Velocity in Inlet Pipe | 1 | m/s
Area Required | 1.2083 | m2
Inlet Pipe Dia required | 1.2407 | m
Provide Inlet Pipe | 2 *700 mm dia | mm
The effective available area for installing tube settler is | 710.8253 | Sq. m
Note: Data in yellow to be reviewed and suitably filled