## Details
Details of Clear Water Pumpling Station
1 | 2 | 3 | 4
S.No. | Details | Value | Units
1 | Design Discharge | 100 | MLD
2 | Pumping Hours | 23 | hours
3 | FSL of CWR | 236 | m
4 | Bed Level of CWR | 232 | m
5 | Size of DI Pipeline | 300 to 1000 | mm
6 | Length of Pipeline | 33000 | m
7 | C value adopted for design purpose | 140
8 | Maximum Operating Head for pumps (Difference in minimum sump level & maximum discharge level+Maximum friction head+ losses in specials, entry & exit) | 50 | m
9 | Minimum Operating head for pumps (Difference in maximum sump level & minimum discharge level+minimum friction head+ losses in specials, entry & exit) | 46 | m
10 | Average Operating Head for pumps | 48 | m
Note; Data in colomn 3 to be appropriately filled

## Sp Speed
Pump Selection based on specific speed and maximum attainable efficiency
Details
Minimum Operating head for pumps (Difference in maximum sump level & minimum discharge level+minimum friction head+ losses in specials, entry & exit) |  |  |  |  | 46 | m
Maximum Operating Head for pumps (Difference in minimum sump level & maximum discharge level+Maximum friction head+ losses in specials, entry & exit) |  |  |  |  | 50 | m
Average Operating Head for pumps |  |  |  |  | 48 | m
Design Discharge |  |  |  |  | 100 | MLD
Pumping Hours |  |  |  |  | 23 | hrs
Calculation of Specific Speed for Different Speeds & Number of Stages
Specific Speed Ns |  | = | N x (Q)0.5/ (H)0.75
where | Q | = | Discharge in US gallon/min
| H | = | Discharge head in feet per stage
| N | = | Motor Speed in rpm
As per American National Standard Institute Hydraulic Institute New Jersey, the specific speed for Pumps should be in the range of 2000 to 3000 for attaining optimum efficiency. Therefore in the present case the duty requirements are to be fixed in such a way so that the specific speed lies in the above range.
Calculation of Specific Speed with different combinations(Items 1 to 5 are VT pumps and items 6&7 are Double Suction HSC pumps)
No of Working Pumps | No of Stages | Discharge per Pump (US GPM) | Pumping Head (ft) | Pumping Head per Stage (feet) | Motor Speed (RPM) | Specific Speed
1 | 1 | 19144.9275 | 157.4803 | 157.4803 | 1500 | 4668.7263
2 | 1 | 9572.4638 | 157.4803 | 157.4803 | 1500 | 3301.288
2 | 1 | 9572.4638 | 157.4803 | 157.4803 | 1000 | 2200.8587
3 | 1 | 6381.6425 | 157.4803 | 157.4803 | 1500 | 2695.4904
2 | 2 | 9572.4638 | 157.4803 | 78.7402 | 1500 | 5552.0826
2 | 1 | 4786.2319 | 157.4803 | 157.4803 | 1500 | 2334.3632
2 | 1 | 4786.2319 | 157.4803 | 157.4803 | 1000 | 1556.2421
Thus single stage VT pump with a speed of 1000 rpm and Double Suction Centrfugal pumps with 2 pumps working have the specific speed in the range of 2000-3000 rpm and are thus the ideal choice. A Single stage Vertical Turbine Pump having Motor Speed of 1500 RPM will have specific speed around 3300, which is slightly higher then upper limit of desired range 2000-3000 for attaining optimum efficiency.However,Pumps & Motors with 1000 RPM speed are more robust compared to 1500 rpm pumping sets. The CWR floor is 3m below GL and in case of Horizontal Split Casing pump, to provide positive suction, pumps have to be installed below this level. The maintenance and shut down time are less in HSC pumps. As such choice is either Single stage VT pumps 1000 rpm with 2W+1S configuration or single stage double suction HSC pump 1500 rpm with 2W+1S configuration. Other alternatives considered above are not suitable on account of very high or lower specific speeds. Morever using single pump with full discharge has 2 drawbacks:(a). Starting current requirement is very high making transformer, cable, switchgear rating high.(b). During initial years of operation, water demand will be less. Thus the pump shall have to operate at full head for a limited period during the day.

## Suction Sp Speed
Suction Specific Speed
As per American National Standard Institute Hydraulic Institute New Jersey, the Suction Specific Speed for V.T. Pumps should be in the vicinity of 8500 for attaining optimum efficiency. Therefore in the present case the duty requirements are to be fixed in such a way so that the Suction Specific Speed be around 8500.
SuctionSpecific Speed (SS) |  | = | N x (Q)0.5/ (NPSHa)0.75
where | Q | = | Discharge in US gallon/min
| H | = | Net Positive Suction Head Available in feet
| N | = | Motor Speed in rpm
For present case
| Q | = | 603.8647 | l/s | = | 9572.4638 | US gallon/min
| N | = | 1000 | rpm
Net Positive Suction Head Available (NPSHa) Required 8500 Suction Specific Speed
Minimum Water Level in CWR |  |  |  |  | = | 232 | m
Minimum Submergence required as per HIS |  |  |  |  | = | 1.55 | m
Bottom level of wet well |  |  |  |  | = | 230.45 | m
Suction Bell mouth Diameter:
Design Velocity |  |  |  |  | = | 1.3 | m/s
Suction Bell mouth Diameter: |  |  |  |  | = | 769.0467 | mm
say | [5 empty] | 350 | mm
Clearance Below suction Bell Mouth (C) as per HIS |  |  |  |  | = | 0.45 | mm
i) Minimum Level in wet well |  |  |  |  | = | 232 | m
ii) Level of suction Bell Mouth |  |  |  |  | = | Bottom Level + Clearance
[5 empty] | = | 230.9 | m
iii) Elevation of eye of impeller |  |  |  |  | = | 231.2 | m
{assumed 0.3 m above (ii)}
iv) Submergence above
eye of impeller [(i) – (iii) ] |  |  |  |  | = | 0.8 | m
v)Losses at inlet Bell mouth(assumed) |  |  |  |  | = | 0.1 | m
vi)Vapor pressure at 320C water temperature (Vp) = | [5 empty] | 0.49 | m
vii)Atmosph. Pressure |  |  |  |  | = | 10.33 | m
NPSH available |  |  |  |  | = | (vii +iv - v - vi )
[5 empty] | = | 10.54 | m
[5 empty] | = | 34.5712 | ft
Specific Speed Ns |  |  |  |  | = | 6862.3999
[5 empty] | = | 4400 | say
Net Positive Suction Head |  |  |  |  | = | 25.9891 | feet
[5 empty] | = | 7.9215 | m
Suction Lift permissible |  |  |  |  | = | 2.0785 | m
= Atmospheric Pressure in m - NPSHA
Thus provide minimum subermergence for Bowl of VT pump

## AttainableEfficiency_EnergyLoad
Attainable Efficiency & Energy Loading
Specific Speed
Specific Speed Ns |  | = | N x (Q)0.5/ (H)0.75
where | Q | = | Discharge in US gallon/min per Pump
| H | = | Discharge head in feet per stage
| N | = | Motor speed in rpm
For present case of Double suction Pump | Q | = | 603.8647 | l/s | = | 9572.4638 | US gallon/min
| H | = | 48 | m per stage | = | 157.4803 | feets
| N | = | 1000 | rpm
Specific Speed Ns |  | = | 2200.8587
As per American Standard for DS Centrifugal Pumps issued by Hydraulic Institute New Jersey, the specific speed for Pumps should be in the range of 2000 to 3000 for attaining optimum efficiency and in the present case the specific speed is within the range specified above.
Generally Attainable Efficiency
As per American Standard for Centrifugal Pumps, generally attainable efficiency for DS Centrifugal Pumps having discharge Q = 9572 g/min & Specific Speed Ns = 2200, is 90% (as per Fig 1.62A, page no. 85).
For discharge Q = 9572 g/min, deviation from generally attainable efficiency is +2% of attainable efficiency (as per Fig 1.63 page no. 85 ) which gives efficiency range from 92% to 88%. The efficiency of pumps is greatly influenced by smoothness of impeller vanes, clearance of impeller ring, effectiveness of stuffing box / mechanical seal and suction arrangement. In view of these factors, the Generally Attainable Efficiency may be taken as 88%.
Proposed Loading for Lower Efficiency
No credit is proposed in the bid evaluation for efficiency offered beyond 88% (without negative tolerance). However we can levy compensation for offering pumps with efficiency less than 88% for each percentage efficiency point.
i) Calculation of Overall Efficiency of Pump Set
Motor Efficiency |  | = | 94% | ( Assuming energy efficient motors)
Pump Efficiency |  | = | 88%
Overall Efficiency |  | = | 0.94 x 0.88
|  | = | 82.72%
|  | = | 82.5%
ii) Motor Power Input Required
|  | = | 9.81QH / n
where | Q | = | Discharge in LPS
| H | = | Discharge head in m
| n | = | Overall Efficiency of Pump Set
|  | = | (603.86 x 9.81 x 48) / (0.825x 1000)
|  | = | 344.664 | KW
|  | = | 345 | KW | say
iii) Calculation of Additional Power Charges
Additional Annual Power charges for lower efficiency |  | = | Differential KW x Annual Working hours x Power Tariff
Differential KW |  | = | (Prescribed Eff - Tendered Eff ) x KW input of Motor / Tendered Eff
Capitalised Additional Power charges for lower efficiency |  | = | Additional Annual Power charges x Annuity Factor
1) Life of Pumpsets is 15 yrs as per CPHEEO mannual.
2) Pumping hours per day = 23 hrs.
Now as Initail Discharge = 59 MLD & Final Discharge = 80 MLD therefore Avg Discharge = 69.5 MLD Average pumping hours for each pump =69.5x23/80=19.98 hours
However as 3 units of pumps are provided (2 working + 1 standby), therefore pumping hours for single pump will be 19.98 x 2 / 3 = 13.33 hrs
Annual Hours of operation of each pump = 13.33 x 365.25 = 4868.78 hrs
3) Annuity Factor
Annuity Factor |  | = | ((1+R)n - 1)/ (R x (1+R)n) |  |  |  | 0
where |  |  | n = no of years =15 yrs |  | R = discounting rate = 10%
Annuity Factor |  | = | 7.6061
4) Power Tariff = Rs. 4.75 per unit
For 1% less effieciency
Differential KW |  | = | (82.5 -81.5) x 345 / 82.5
|  | = | 4.1818 | KW
Additional Annual Power charges for lower efficiency |  | = | 4.1818x4868.78x4.75
|  | = | 96711.7251 | (Rs.)
Capitalised Additional Power charges |  | = | 96712 x 7.606
|  | = | 735597.0704 | (Rs.) | For each percentage point of less efficiency.

## Motor Rating
Motor Rating
Pump Discharge |  | = | 603.86 | LPS
Design Head |  | = | 48 | m
Motor Efficiency |  |  | 94% | ( Assuming energy efficient motors)
Pump Efficiency |  | = | 88%
Overall Efficiency |  | = | 0.94 x 0.88
|  | = | 82.72%
Motor Power Input Required
|  | = | 9.81QH / n
where | Q | = | Discharge in LPS
| H | = | Discharge head in m
| n | = | Pump Efficiency
|  | = | 343.7447 | KW
|  | = | 344 | KW | say
The motor rating shall be higher of the following:
1. 110% of Input Power requirement at duty point.
2. Maximum Power requirement in the entire working range of the pump.
The Motor rating required as per first alternative is 378.11 KW. Thus we go for next available rating of 380KW.

## CRANE Capacity
Crane Capacity
a) Static Load of Pump Motor Set
i) Weight of pump assembly (from Kirloskar cataloge approx) |  |  | = | 2550 | kg
ii) Weight of line shaft and coupling, |  |  | = | 300 | kg
(0.7854 x 0.082(d)x 5(L) x 7850 + 100 kg for couplings)
iii) Line Shaft Bearings (Approx) |  |  | = | 50 | kg
iv) Weight of Column Pipe and Flanges |  |  | = | 600 | kg
(Length 5.0 m, Thickness 8mm, Dia 500 mm, Flanges 4 No)
ii) Discharge Head Weight (Assumed) |  |  | = | 1000 | kg
ii) Weight of 380 kW motor |  |  | = | 2500 | kg
vii) Weight of Structural steel and Sole Plate |  |  | = | 1000 | kg
viii) Weight of water in column pipe and bowl assembly |  |  | = | 120 | kg
(D = 350 mm, L = 6.0 m)
As per IS 2974 (Part IV)- 1979, Code of Practice for Design and Construction of Machine
Dynamic Factors for Pump, Motor etc are as follows
Pump – 3 | These are basically applicable for Centrifugal Pumps. Judicious assumptions are necessary for VT Pumps.
Motor – 2
Based on above the Dynamic Factors considered are
Bowl Assembly |  |  | = | 3
Line Shaft and Bearings |  |  | = | 3
Motor |  |  | = | 2
Column Pipe and Flanges |  |  | = | 1.5
Discharge Head / Motor Stool |  |  | = | 1.5
Other |  |  | = | 1
Hence Dynamic Load of Pump – Motor Set
= (i) x 3 + (ii) x 3 + (iii) x 3 + (iv) x 1.5 + (v) x 1.5 +(vi) x 2 +(vii) x 1 + (viii) x 1
|  |  | = | 17220 | kg
Keeping margin about 20 % for unaccounted dynamic load for vibrations, pulsations etc.
Design dynamic load |  |  | = | 20664 | kg
|  | say | = | 18000 | kg
b) Crane Capacity
Maximum weight to be handled by crane |  |  | = | Greater of (i) & (ii)
|  |  | = | 2550 | Kg
Considering 25 % over loading |  |  | = | 3187.5 | kg
|  | say | = | 5000 | kg
Provide crane of 5000 kg ( 5.0 T ) safe working load.