## Water Demand
Water Demand
Year | Population | LPCD | Losses | Demand | Losses | Fire Demand | Total | Present Source | Deficit
|  |  | % | MLD | MLD | MLD | MLD | MLD | MLD
2011 | 303092 | 135 | 45 | 40.9174 | 18.4128 | 1.741 | 61.0712 | 81.05 | 0
2016 | 323107 | 135 | 45 | 43.6194 | 19.6288 | 1.7975 | 65.0457 | 60.79 | 4.2557
2021 | 344444 | 135 | 35 | 46.4999 | 16.275 | 1.8559 | 64.6308 | 45.5906 | 19.0402
2026 | 364535 | 135 | 25 | 49.2122 | 12.3031 | 1.9093 | 63.4246 | 34.193 | 29.2316
2031 | 385795 | 135 | 15 | 52.0823 | 7.8123 | 1.9642 | 61.8588 | 25.6447 | 36.2141
2036 | 405945 | 135 | 15 | 54.8026 | 8.2204 | 2.0148 | 65.0378 | 19.2335 | 45.8042
2041 | 427147 | 135 | 15 | 57.6648 | 8.6497 | 2.0668 | 68.3813 | 14.4252 | 53.9562
Note: Data in yellow boxes are to be suitably filled for particular case
Assumptions: i) LPCD provides 135 or 150 LPCD for population less than 100000 or more as per manual
ii) Losses at present can be changed as per actual. After 5 years losses remain same % as before
as reduction takes long time but after that losses reduce by absolute 10% till it stabilizes
at minimum 15% level
iii) Fire demand taken as per formula given in manual
iv) present source to be taken at actual and in future estimate present source