## Pumping Station
Tool for Design of Sewage Pumping Station
Guidance: In yellow cells information to be filled as per particular requirement. In green cells review the information and update/revise if needed.
Sr. no | Design of Sewage Lifting Station | Unit | PS -1 | PS -2 | PS -3
A | Input Information: In yellow cells information to be filled as per particular requirement
1 | Peak Sewage flow | lps | 43.7 | 81.69 | 1173.11
2 | Peak factor |  | 3 | 2.5 | 2.25
3 | Liquid depth in wet well assumed | m | 2.2 | 2.2 | 2.2
9 | Invert Level | m | 207.4982 | 207.4982 | 202.7611
10 | Ground Level | m | 211 | 211 | 207
11 | Delivery length of pumping Main | m | 150 | 150 | 600
12 | Level of Delivery Point above GL of SPS | m | 7 | 7 | 7.5
B | Review/Update If needed: In green cells review information and update if needed
4 | Detention time in Wetwell | mins | 20 | 20 | 20
5 | Velocity of flow during peak flow | m/s | 1.2 | 1.2 | 1.2
6 | Velocity of flow during average flow | m/s | 0.8 | 0.8 | 0.8
7 | Proposed pumps Working | numbers | 2 | 2 | 2
8 | Stand by pumps |  | 100% | 100% | 100%
13 | Material of pumping Main pipe |  | HDPE | HDPE | HDPE
C | Design of Sewage Pumping Station
1 | Peak Sewage flow | lpd | 3775680 | 7058016 | 101356704
2 | Average Sewage flow | lpd | 1258560 | 2823206.4 | 45047424
3 | Average Sewage flow | lps | 14.5667 | 32.676 | 521.3822
Wetwell Design
5 | Volume of the Wetwell Required | Cum | 17.48 | 39.2112 | 625.6587
7 | Area of the Wetwell Required | Sq.m | 7.9455 | 17.8233 | 284.3903
8 | Diameter of the wetwell | m | 3.1806 | 4.7637 | 19.0288
9 | Diameter of the wetwell, say | m | 3.5 | 5 | 19.5
10 | Diameter of pumping main for average flow | mm | 152.2615 | 228.0471 | 910.9366
11 | Diameter of pumping main for peak flow | mm | 215.3303 | 294.4075 | 1115.665
12 | Average dia for peak & average flow | mm | 183.7959 | 261.2273 | 1013.3008
13 | Dia of pumping main | m | 0.2 | 0.3 | 1.1
14 | Area of pumping main pipe | Sq. m | 0.031416 | 0.070686 | 0.95033
15 | Velocity in pipe for peak flow | m/s | 1.391 | 1.1557 | 1.2344
16 | Discharge in each Pump | lps | 21.85 | 40.845 | 586.555
17 | Discharge in each Pump | cum/hr | 78.7 | 147.1 | 2111.6
18 | Discharge in each Pump, say | cum/hr | 80 | 150 | 2120
19 | Pumping Head | m | 11.5 | 11 | 12.5
Hydraulic Details
20 | Depth | m | 3.5018 | 3.5018 | 4.2389
21 | Head loss | m | 0.59899 | 0.42144 | 0.43459
22 | Total head required | m | 11.1008 | 10.9232 | 12.1735
23 | HP required |  | 7 | 12 | 200
24 | Diameter of the pipe proposed | mm | 200 | 270 | 1100
D | Output Table
1 | Diameter of the wetwell | m | 3.5 | 5 | 19.5
2 | Discharge in each Pump | cum/hr | 80 | 150 | 2120
3 | Pumping Head | m | 11.5 | 11 | 12.5
4 | HP required |  | 7 | 12 | 200
5 | Diameter of the pipe proposed | mm | 200 | 270 | 1100